## bus
| name | vn_kv | type | zone | in_service | geo
0 | Bus 0 | 110 | b | CIGRE_MV | TRUE | "{\"coordinates\":[7.0,16.0], \"type\":\"Point\"}"
1 | Bus 1 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [4.0, 15.0], \"type\": \"Point\"}"
2 | Bus 2 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [4.0, 13.0], \"type\": \"Point\"}"
3 | Bus 3 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [4.0, 11.0], \"type\": \"Point\"}"
4 | Bus 4 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [2.5, 9.0], \"type\": \"Point\"}"
5 | Bus 5 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [1.0, 7.0], \"type\": \"Point\"}"
6 | Bus 6 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [1.0, 3.0], \"type\": \"Point\"}"
7 | Bus 7 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [8.0, 3.0], \"type\": \"Point\"}"
8 | Bus 8 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [8.0, 5.0], \"type\": \"Point\"}"
9 | Bus 9 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [6.0, 5.0], \"type\": \"Point\"}"
10 | Bus 10 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [4.0, 5.0], \"type\": \"Point\"}"
11 | Bus 11 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [4.0, 7.0], \"type\": \"Point\"}"
12 | Bus 12 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [10.0, 15.0], \"type\": \"Point\"}"
13 | Bus 13 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [10.0, 11.0], \"type\": \"Point\"}"
14 | Bus 14 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [10.0, 5.0], \"type\": \"Point\"}"

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | Load R1 | 1 | 14.994 | 3.0447 | 0 | 0 | 15.3 | 1 | TRUE | wye
1 | Load R3 | 3 | 0.27645 | 0.069285 | 0 | 0 | 0.285 | 1 | TRUE | wye
2 | Load R4 | 4 | 0.43165 | 0.10818 | 0 | 0 | 0.445 | 1 | TRUE | wye
3 | Load R5 | 5 | 0.7275 | 0.18233 | 0 | 0 | 0.75 | 1 | TRUE | wye
4 | Load R6 | 6 | 0.54805 | 0.13735 | 0 | 0 | 0.565 | 1 | TRUE | wye
5 | Load R8 | 8 | 0.58685 | 0.14708 | 0 | 0 | 0.605 | 1 | TRUE | wye
6 | Load R10 | 10 | 0.4753 | 0.11912 | 0 | 0 | 0.49 | 1 | TRUE | wye
7 | Load R11 | 11 | 0.3298 | 0.082656 | 0 | 0 | 0.34 | 1 | TRUE | wye
8 | Load R12 | 12 | 14.994 | 3.0447 | 0 | 0 | 15.3 | 1 | TRUE | wye
9 | Load R14 | 14 | 0.20855 | 0.052268 | 0 | 0 | 0.215 | 1 | TRUE | wye
10 | Load CI1 | 1 | 4.845 | 1.5925 | 0 | 0 | 5.1 | 1 | TRUE | wye
11 | Load CI3 | 3 | 0.22525 | 0.1396 | 0 | 0 | 0.265 | 1 | TRUE | wye
12 | Load CI7 | 7 | 0.0765 | 0.04741 | 0 | 0 | 0.09 | 1 | TRUE | wye
13 | Load CI9 | 9 | 0.57375 | 0.35558 | 0 | 0 | 0.675 | 1 | TRUE | wye
14 | Load CI10 | 10 | 0.068 | 0.042143 | 0 | 0 | 0.08 | 1 | TRUE | wye
15 | Load CI12 | 12 | 5.016 | 1.6487 | 0 | 0 | 5.28 | 1 | TRUE | wye
16 | Load CI13 | 13 | 0.034 | 0.021071 | 0 | 0 | 0.04 | 1 | TRUE | wye
17 | Load CI14 | 14 | 0.3315 | 0.20545 | 0 | 0 | 0.39 | 1 | TRUE | wye

## switch
| bus | element | et | type | closed | name | z_ohm | in_ka
0 | 6 | 12 | l | LBS | TRUE |  | 0
1 | 7 | 12 | l | LBS | FALSE | S2 | 0
2 | 4 | 13 | l | LBS | FALSE | S3 | 0
3 | 11 | 13 | l | LBS | TRUE |  | 0
4 | 8 | 14 | l | LBS | FALSE | S1 | 0
5 | 14 | 14 | l | LBS | TRUE |  | 0
6 | 0 | 0 | t | CB | TRUE |  | 0
7 | 0 | 1 | t | CB | TRUE |  | 0

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service | controllable | s_sc_max_mva | s_sc_min_mva | rx_min | rx_max
0 |  | 0 | 1.03 | 0 | 1 | TRUE | FALSE | 5000 | 5000 | 0.1 | 0.1

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service | geo
0 | Line 1-2 | CABLE_CIGRE_MV | 1 | 2 | 2.82 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE | NaN
1 | Line 2-3 | CABLE_CIGRE_MV | 2 | 3 | 4.42 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE | NaN
2 | Line 3-4 | CABLE_CIGRE_MV | 3 | 4 | 0.61 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE | NaN
3 | Line 4-5 | CABLE_CIGRE_MV | 4 | 5 | 0.56 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE | NaN
4 | Line 5-6 | CABLE_CIGRE_MV | 5 | 6 | 1.54 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE | NaN
5 | Line 7-8 | CABLE_CIGRE_MV | 7 | 8 | 1.67 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE | NaN
6 | Line 8-9 | CABLE_CIGRE_MV | 8 | 9 | 0.32 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE | NaN
7 | Line 9-10 | CABLE_CIGRE_MV | 9 | 10 | 0.77 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE | NaN
8 | Line 10-11 | CABLE_CIGRE_MV | 10 | 11 | 0.33 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE | NaN
9 | Line 3-8 | CABLE_CIGRE_MV | 3 | 8 | 1.3 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE | NaN
10 | Line 12-13 | OHL_CIGRE_MV | 12 | 13 | 4.89 | 0.51 | 0.366 | 10.0968 | 0 | 0.195 | 1 | 1 | ol | TRUE | NaN
11 | Line 13-14 | OHL_CIGRE_MV | 13 | 14 | 2.99 | 0.51 | 0.366 | 10.0968 | 0 | 0.195 | 1 | 1 | ol | TRUE | NaN
12 | Line 6-7 | CABLE_CIGRE_MV | 6 | 7 | 0.24 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE | NaN
13 | Line 11-4 | CABLE_CIGRE_MV | 11 | 4 | 0.49 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE | NaN
14 | Line 14-8 | OHL_CIGRE_MV | 14 | 8 | 2 | 0.51 | 0.366 | 10.0968 | 0 | 0.195 | 1 | 1 | ol | TRUE | NaN

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_changer_type | id_characteristic_table | tap_dependency_table | parallel | df | in_service
0 | Trafo 0-1 |  | 0 | 1 | 25 | 110 | 20 | 12.0011 | 0.16 | 0 | 0 | 30 | [9 empty] | FALSE | 1 | 1 | TRUE
1 | Trafo 0-12 |  | 0 | 12 | 25 | 110 | 20 | 12.0011 | 0.16 | 0 | 0 | 30 | [9 empty] | FALSE | 1 | 1 | TRUE

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV
CABLE_CIGRE_MV | 151.1749 | 0.501 | 0.716 | 0.145 | cs
OHL_CIGRE_MV | 10.0968 | 0.51 | 0.366 | 0.195 | ol

## line_dc_std_types
| r_ohm_per_km | max_i_ka | type | q_mm2 | alpha
95-CU | 0.193 | 0.404 | cs | 95 | 0.00393
400-CU | 0.047 | 0.922 | cs | 400 | 0.00393
1200-CU | 0.0151 | 1.791 | cs | 1200 | 0.00393
2400-CU | 0.0073 | 2.678 | cs | 2400 | 0.00393
95-AL | 0.32 | 0.31 | cs | 95 | 0.00403
400-AL | 0.0778 | 0.705 | cs | 400 | 0.00403
1200-AL | 0.0247 | 1.371 | cs | 1200 | 0.00403
2400-AL | 0.0121 | 2.066 | cs | 2400 | 0.00403

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_changer_type | trafo_characteristic_table
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | Ratio | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | Ratio | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | Ratio | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | Ratio | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | Ratio | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | Ratio | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | Ratio | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | Ratio | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | Ratio | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | Ratio | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | Ratio | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | Ratio | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | Ratio | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | Ratio | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_changer_type | trafo_characteristic_table
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2 | Ratio | FALSE
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2 | Ratio | FALSE

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1.03 | 0 | -45.0457 | -16.3414
1 | 0.99197 | -36.5568 | 19.839 | 4.6371
2 | 0.96815 | -37.6042 | 0 | 0
3 | 0.93096 | -39.331 | 0.5017 | 0.20888
4 | 0.9291 | -39.435 | 0.43165 | 0.10818
5 | 0.92782 | -39.5066 | 0.7275 | 0.18233
6 | 0.92632 | -39.5918 | 0.54805 | 0.13735
7 | 0.92512 | -39.5896 | 0.0765 | 0.04741
8 | 0.9254 | -39.579 | 0.58685 | 0.14708
9 | 0.92442 | -39.6192 | 0.57375 | 0.35558
10 | 0.92317 | -39.6854 | 0.5433 | 0.16126
11 | 0.92298 | -39.6965 | 0.3298 | 0.082656
12 | 1.0001 | -35.4871 | 20.01 | 4.6933
13 | 0.99533 | -35.5382 | 0.034 | 0.021071
14 | 0.99255 | -35.5679 | 0.54005 | 0.25771

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 4.5489 | 1.5043 | -4.4662 | -1.4376 | 0.082686 | 0.066705 | 0.13943 | 0.1399 | 0.1399 | 0.99197 | -36.5568 | 0.96815 | -37.6042 | 96.483
1 | 4.4662 | 1.4376 | -4.3355 | -1.3266 | 0.1307 | 0.11105 | 0.1399 | 0.14059 | 0.14059 | 0.96815 | -37.6042 | 0.93096 | -39.331 | 96.9588
2 | 1.712 | 0.3865 | -1.7093 | -0.39264 | 0.002719 | -0.0061376 | 0.054423 | 0.054492 | 0.054492 | 0.93096 | -39.331 | 0.9291 | -39.435 | 37.5807
3 | 1.2777 | 0.28446 | -1.2763 | -0.29164 | 0.0013943 | -0.0071781 | 0.040669 | 0.040732 | 0.040732 | 0.9291 | -39.435 | 0.92782 | -39.5066 | 28.091
4 | 0.54876 | 0.10931 | -0.54805 | -0.13344 | 0.00070803 | -0.024132 | 0.017409 | 0.017578 | 0.017578 | 0.92782 | -39.5066 | 0.92632 | -39.5918 | 12.1229
5 | -0.0765 | -0.04741 | 0.076517 | 0.020274 | 1.7101e-05 | -0.027136 | 0.0028084 | 0.0024693 | 0.0028084 | 0.92512 | -39.5896 | 0.9254 | -39.579 | 1.9368
6 | 1.449 | 0.57156 | -1.4478 | -0.57514 | 0.0011369 | -0.0035757 | 0.048589 | 0.048649 | 0.048649 | 0.9254 | -39.579 | 0.92442 | -39.6192 | 33.5509
7 | 0.87408 | 0.21956 | -0.87316 | -0.23073 | 0.00091978 | -0.011169 | 0.028143 | 0.028241 | 0.028241 | 0.92442 | -39.6192 | 0.92317 | -39.6854 | 19.4763
8 | 0.32986 | 0.069463 | -0.3298 | -0.074726 | 5.5292e-05 | -0.0052627 | 0.010541 | 0.010576 | 0.010576 | 0.92317 | -39.6854 | 0.92298 | -39.6965 | 7.2941
9 | 2.1218 | 0.7312 | -2.1123 | -0.73891 | 0.0094922 | -0.0077109 | 0.069591 | 0.069808 | 0.069808 | 0.93096 | -39.331 | 0.9254 | -39.579 | 48.1436
10 | 0.57797 | 0.26917 | -0.57543 | -0.27352 | 0.0025442 | -0.0043506 | 0.018403 | 0.018479 | 0.018479 | 1.0001 | -35.4871 | 0.99533 | -35.5382 | 9.4762
11 | 0.54143 | 0.25245 | -0.54005 | -0.25521 | 0.001377 | -0.0027597 | 0.017326 | 0.017372 | 0.017372 | 0.99533 | -35.5382 | 0.99255 | -35.5679 | 8.9089
12 | 1.3401e-09 | -0.0039122 | 3.2461e-13 | -2.6846e-13 | 1.3404e-09 | -0.0039122 | 0.00012192 | 1.3127e-14 | 0.00012192 | 0.92632 | -39.5918 | 0.92632 | -39.5918 | 0.084082
13 | 1.1326e-08 | -0.00793 | 1.7441e-13 | 1.2796e-13 | 1.1326e-08 | -0.00793 | 0.00024802 | 6.7657e-15 | 0.00024802 | 0.92298 | -39.6965 | 0.92298 | -39.6967 | 0.17105
14 | 4.0442e-09 | -0.0024999 | 7.7109e-14 | 8.3583e-14 | 4.0442e-09 | -0.0024999 | 7.2709e-05 | 3.3074e-15 | 7.2709e-05 | 0.99255 | -35.5679 | 0.99256 | -35.5681 | 0.037287

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 24.4291 | 9.2268 | -24.3879 | -6.1415 | 0.041137 | 3.0853 | 0.13307 | 0.73187 | 1.03 | 0 | 0.99197 | -36.5568 | 101.4115
1 | 20.6167 | 7.1146 | -20.588 | -4.9625 | 0.028695 | 2.1521 | 0.11114 | 0.61126 | 1.03 | 0 | 1.0001 | -35.4871 | 84.698

## res_ext_grid
| p_mw | q_mvar
0 | 45.0457 | 16.3414

## res_load
| p_mw | q_mvar
0 | 14.994 | 3.0447
1 | 0.27645 | 0.069285
2 | 0.43165 | 0.10818
3 | 0.7275 | 0.18233
4 | 0.54805 | 0.13735
5 | 0.58685 | 0.14708
6 | 0.4753 | 0.11912
7 | 0.3298 | 0.082656
8 | 14.994 | 3.0447
9 | 0.20855 | 0.052268
10 | 4.845 | 1.5925
11 | 0.22525 | 0.1396
12 | 0.0765 | 0.04741
13 | 0.57375 | 0.35558
14 | 0.068 | 0.042143
15 | 5.016 | 1.6487
16 | 0.034 | 0.021071
17 | 0.3315 | 0.20545

## res_switch
| i_ka | loading_percent | p_from_mw | q_from_mvar | p_to_mw | q_to_mvar
0 | 0.00012192
1 | 0
2 | 0
3 | 0.00024802
4 | 0
5 | 7.2709e-05
6 | 0.13307
7 | 0.11114

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | bus | geo | object
6 | load | name | object
7 | load | bus | uint32
8 | load | p_mw | float64
9 | load | q_mvar | float64
10 | load | const_z_percent | float64
11 | load | const_i_percent | float64
12 | load | sn_mva | float64
13 | load | scaling | float64
14 | load | in_service | bool
15 | load | type | object
16 | switch | bus | int64
17 | switch | element | int64
18 | switch | et | object
19 | switch | type | object
20 | switch | closed | bool
21 | switch | name | object
22 | switch | z_ohm | float64
23 | switch | in_ka | float64
24 | ext_grid | name | object
25 | ext_grid | bus | uint32
26 | ext_grid | vm_pu | float64
27 | ext_grid | va_degree | float64
28 | ext_grid | slack_weight | float64
29 | ext_grid | in_service | bool
30 | ext_grid | controllable | bool
31 | ext_grid | s_sc_max_mva | float64
32 | ext_grid | s_sc_min_mva | float64
33 | ext_grid | rx_min | float64
34 | ext_grid | rx_max | float64
35 | line | name | object
36 | line | std_type | object
37 | line | from_bus | uint32
38 | line | to_bus | uint32
39 | line | length_km | float64
40 | line | r_ohm_per_km | float64
41 | line | x_ohm_per_km | float64
42 | line | c_nf_per_km | float64
43 | line | g_us_per_km | float64
44 | line | max_i_ka | float64
45 | line | df | float64
46 | line | parallel | uint32
47 | line | type | object
48 | line | in_service | bool
49 | line | geo | object
50 | trafo | name | object
51 | trafo | std_type | object
52 | trafo | hv_bus | uint32
53 | trafo | lv_bus | uint32
54 | trafo | sn_mva | float64
55 | trafo | vn_hv_kv | float64
56 | trafo | vn_lv_kv | float64
57 | trafo | vk_percent | float64
58 | trafo | vkr_percent | float64
59 | trafo | pfe_kw | float64
60 | trafo | i0_percent | float64
61 | trafo | shift_degree | float64
62 | trafo | tap_side | object
63 | trafo | tap_neutral | float64
64 | trafo | tap_min | float64
65 | trafo | tap_max | float64
66 | trafo | tap_step_percent | float64
67 | trafo | tap_step_degree | float64
68 | trafo | tap_pos | float64
69 | trafo | tap_changer_type | object
70 | trafo | id_characteristic_table | Int64
71 | trafo | tap_dependency_table | bool
72 | trafo | parallel | uint32
73 | trafo | df | float64
74 | trafo | in_service | bool
75 | res_bus | vm_pu | float64
76 | res_bus | va_degree | float64
77 | res_bus | p_mw | float64
78 | res_bus | q_mvar | float64
79 | res_line | p_from_mw | float64
80 | res_line | q_from_mvar | float64
81 | res_line | p_to_mw | float64
82 | res_line | q_to_mvar | float64
83 | res_line | pl_mw | float64
84 | res_line | ql_mvar | float64
85 | res_line | i_from_ka | float64
86 | res_line | i_to_ka | float64
87 | res_line | i_ka | float64
88 | res_line | vm_from_pu | float64
89 | res_line | va_from_degree | float64
90 | res_line | vm_to_pu | float64
91 | res_line | va_to_degree | float64
92 | res_line | loading_percent | float64
93 | res_trafo | p_hv_mw | float64
94 | res_trafo | q_hv_mvar | float64
95 | res_trafo | p_lv_mw | float64
96 | res_trafo | q_lv_mvar | float64
97 | res_trafo | pl_mw | float64
98 | res_trafo | ql_mvar | float64
99 | res_trafo | i_hv_ka | float64
100 | res_trafo | i_lv_ka | float64
101 | res_trafo | vm_hv_pu | float64
102 | res_trafo | va_hv_degree | float64
103 | res_trafo | vm_lv_pu | float64
104 | res_trafo | va_lv_degree | float64
105 | res_trafo | loading_percent | float64
106 | res_ext_grid | p_mw | float64
107 | res_ext_grid | q_mvar | float64
108 | res_load | p_mw | float64
109 | res_load | q_mvar | float64
110 | res_switch | i_ka | float64
111 | res_switch | loading_percent | float64
112 | res_switch | p_from_mw | float64
113 | res_switch | q_from_mvar | float64
114 | res_switch | p_to_mw | float64
115 | res_switch | q_to_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 3.1.1 | 3.0.0 | TRUE | FALSE |  | 50 | 1